## Version Control
Document name | Electrical Infrastructure Innovation Roadmap
Document Number | PN000201-ANA-001
Issue Number | 3
Issue No: | Date Issued: | Author | Approver | Revision History
1 | 2018-02-28 | K. Stefaniak | J. Flowers | First Issued
2 | 2018-10-25 | K. Stefaniak | A. Stormonth-Darling | Second Issued
3 | 2019-04-05 | K. Stefaniak | A. Stormonth-Darling | Third Issued
Disclaimer Notice
Whilst the information contained in this report has been prepared and collated in good faith. The Offshore Wind Innovation Hub makes no representation or warranty (express or implied) as to the accuracy or completeness of the information contained herein nor shall we be liable for any loss or damage resultant from reliance on same.

## Electrical Infrastructure
Description | Type of Entry | Start TRL | Target TRL | Enabler | Beneficiary | Strategic Outcome | Notes | Website | Forecast Start | Forecast Finish | Potential to Reduce LCoE | UK Benefit | Case for Intervention | HSE Impact | Potential to Reduce LCoE (comments) | UK Benefit (comments) | Case for Intervention (comments) | HSE impact (comments)
Electrical Infrastructure
Component Reliability Improvement
Cables
Improved standards of cables | Innovation Area | TRL 7 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising >15MW turbine platforms | Seek improvement of offshore wind subsea power cables standards including all types of pre-commercial and factory testing. |  | 2019 | 2033 | H | L | H | L |  |  |  | Improved design would lead to less failures and decreased frequency of underwater inspection
Representative accelerated testing of cables | Innovation Area | TRL 4 | TRL 9 | Catapult | Owner Operators | Commercialising >15MW turbine platforms | Develop more representative cable testing methodologies to better understand failure mechanisms (e.g. better representation of loading conditions with simultaneous electrical and mechanical stress) and recommend mitigation measures and solutions. |  | 2019 | 2023 | H | L | H | n/a
Understanding of root cause of cables failures | Innovation Area | TRL 5 | TRL 7 | Catapult | Owner Operators | Commercialising >15MW turbine platforms | Better understanding of loading conditions, fault location and failure mode of subsea power cables. |  | 2019 | 2020 | H | L | M | n/a
Insulation degradation | Ongoing R&D project | TRL 1 | TRL 4 | Academia | Owner Operators | Commercialising >15MW turbine platforms | Rapid and transformative advances in power electronic systems are currently taking place following technological breakthroughs in wide-bandgap (WBG) power semiconductor devices. The enhancements in switching speed and operating temperature, and reduction and lifetime of inverter-fed machines with fast switching (high dv/dt) converters. Note: TRLs for this project have not been updated. | https://gtr.ukri.org/projects?ref=EP%2FS00081X%2F1 | 2019 | 2021
Comρonents
Development of components health monitoring | Innovation Area | TRL 4 | TRL 6 | Research Technical Organisations | Owner Operators | Enabling disruptive innovation | Integration of electrical infrastructure component condition-based health monitoring (CBHM) into a single intelligent platform. Development of new solutions. Relatively new area, with big SMEs opportunities. |  | 2019 | 2023 | M | H | M | M |  |  |  | Decreased number and scale of marine operations
Demonstration of components health monitoring | Innovation Area | TRL 5 | TRL 7 | Industry/SMEs | Owner Operators | Maximising operational performance of existing wind farms | Implementation of integrated condition based health monitoring (CBHM) dedicated to the electrical equipment of turbines. For example, development of integrated power quality or converter' power electronic monitoring within the turbines. Area with big potential and opportunities to SMEs. |  | 2019 | 2025 | M | H | M | M |  |  |  | Decreased number and scale of marine operations
Subsea connectors | Innovation Area | TRL 5 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Subsea cable connector is a key contributor to subsea cable repair. Usually it is provided by the corresponding wind farm export cable manufacturer. Once cable fault happens, it takes time to coordinate necessary repair with the manufacturer and financial losses rise due to cable downtime. Universal subsea connectors will greatly reduce the cost of itself, improve the cable repair efficiency and reduce wind farm downtime. Sector such as Tidal and Wave can benefit from improved design solutions, and demonstration these in a representative environment. |  | 2019 | 2028 | L | M | L | M |  |  |  | Designed to reduce environmental impact
Offshore Substation Optimisation
Optimised Designs
HVDC Convertor Platform optimisation | Innovation Area | TRL 6 | TRL 8 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | HVDC Converter Platform and overall System Optimisation; lessons learned from other markets into UK future projects |  | 2019 | 2023 | H | M | M | L |  |  |  | Standardised design would result in operators being more familiar with setups and small impact on H&S
Standardisation of HVAC | Innovation Area | TRL 7 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising >15MW turbine platforms | Standardised AC Offshore Substation Designs; Lessons learned from UK and European projects and evolution from ad-hoc designs to modular repetitive solutions. |  | 2019 | 2023 | H | L | M | n/a |  |  |  | Mostly a cost concern
DC Arrays
HVDC Interface | Innovation Area | TRL 3 | TRL 5 | Academia | Original Equipment Manufacturers | Enabling disruptive innovation | HVDC Interarray Grid (above equivalent of a 66kV AC grid). Challenge: develop convertor and switchgear within WTG. Goal: to eliminate the AC/DC platform for far from shore offshore wind farms to reduce costs and improve reliabilities |  | 2019 | 2033 | H | L | M | L |  |  |  | It will slightly reduce number of equipment offshore
MVDC Interface | Innovation Area | TRL 3 | TRL 5 | Academia | Original Equipment Manufacturers | Enabling disruptive innovation | MVDC Interarray Grid (Up to equivalent of 66kV AC grid). Challenge: develop convertor and switchgear within WTG. Goal: to eliminate the AC/DC platform and significantly reduce costs for medium distance wind farms. An intermediate step to get HVDC Interface |  | 2019 | 2023 | H | L | M | L |  |  | Successful intervention would increase UK benefit to High | It will slightly reduce number of equipment offshore
MVDC Protection | Innovation Area | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Offshore DC Array Architecture - Protection methods, breakers. Develop designs. Reduction of electrical stresses, but mechanical stresses would remain the same. Reduce number of components to reduce costs. It is a safety system, but not designed to protect human intervention |  | 2019 | 2023 | M | M | H | n/a
Future Internal Array Systems
Maturing of 66kV market
66kV Components for cost effective 66 kV array solutions | Innovation Area | TRL 6 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Develop 66kV Components ( including cable, circuit breaker, space saving switchgear and cast resin 66/72 offshore transformer) to improve efficiency, reliability and operation |  | 2019 | 2023 | M | L | M | L |  |  |  | Reduced environmental impact
Dynamic 66kVAC Cables | Innovation Area | TRL 6 | TRL 9 | Industry/SMEs | Owner Operators | Maximising operational performance of existing wind farms | Dynamic 66kVAC cables are used for the floating wind turbine array cable. Due to the floating platform, the wind turbine export cable will suffer stresses from wind, wave and current. Currently, the cable failure mechanism is not well understood. It requires aerodynamic, hydrodynamic, material and electrical background to investigate the cable failure. Thereby, the margin can be well designed. The reliability of the cable could be achieved in more economical way. Help cable manufacturers in their R&D activities to qualify and test cables (e.g. use of dynamic cable test rig) but also promote new market entrants. |  | 2019 | 2023 | M | M | L | L |  |  |  | Reduced environmental impact
Next Generation Array Systems
66kV+ Cables & Components | Innovation Area | TRL 5 | TRL 7 | Research Technical Organisations | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Distribution voltages beyond 66kV Including cable, circuit breaker and switchgear - Demonstration for floating wind (and tidal) and distribution voltages beyond 66kV. This is geared towards the potential future needs for very large far offshore floating wind farms to reduce costs and increase efficiencies |  | 2019 | 2023 | M | L | H | L |  |  |  | Less copper used results in small impact on environmental issues
Dynamic cables | Innovation Area | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Help cable manufactures in qualifying their dynamic cable technologies in a representative environment. This shall address the need of floating wind, tidal and wave generation. |  | 2019 | 2033 | M | L | H | n/a
Flexible Offshore Wind Solutions
New revenue streams and MWh optimisation
Hybrid synchronous compensator | Innovation Area | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Provision of Ancillary Services along a wind farm by means of hybrid synchronous compensator arrangement (with storage and Statcom). |  | 2019 | 2021 | M | M | M | n/a
Smart energy systems | Innovation Area | TRL 6 | TRL 8 | Research Technical Organisations | Owner Operators | Maximising operational performance of existing wind farms | Cyber Security and Network Automation Solutions for offshore wind. Develop standards, demonstration, etc. - Pre-cursor to smart systems. New business models and commercial arrangements. |  | 2019 | 2025 | M | M | M | L | Medium-High
Turbine level storage | Innovation Area | TRL 4 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Variable wind speed leads to variable power generation, frequency deviations and voltage fluctuation, which are one of main problems related to wind energy integration into a grid. Wind farms have to provide support during grid instability and transients. Turbine level storage would increase the lifetime of turbine components. It would also increase amount of energy integrated into a grid. Biggest challenge in this area is to produce simulation modelling. These solutions would be also applicable into wave & tidal devices. |  | 2019 | 2023 | H | M | L | M |  |  |  | Turbines would be more reliable and wouldn’t require urgent marine operations if it loses connection to the grid.
Windfarm co-located energy storage systems | Innovation Area | TRL 5 | TRL 7 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Demonstration of onshore storage for Offshore Wind Farms. Including demonstration/elimination of onshore STATCOM |  | 2019 | 2021 | H | M | M | L
Alternatives Grid Solutions
Other Alternatives to Grid
Low frequency AC transmission | Innovation Area | TRL 5 | TRL 7 | Research Technical Organisations | Owner Operators | Enabling disruptive innovation | The use of low frequency AC for transmitting offshore wind power from long distances. This includes AC equipment dimensioning, and wind turbine operation in low frequency grids. The purpose is to improve efficiency of transmission. |  | 2019 | 2022 | H | M | M | n/a | Some reports (112843-UKBR-R-01-F). points out there could be a potential significant cost reduction if low frequency AC is used |  | The outcome of the new offshore HVDC projects currently under development may have a significant impact on the pursue of LFAC transmission
PROMOTioN - Progress on Meshed HVDC Offshore Transmission Networks | Ongoing R&D project | TRL 1 | TRL 1 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | In order to unlock the full potential of Europe’s offshore resources, network infrastructure is urgently required, linking off-shore wind parks and on-shore grids in different countries. HVDC technology is envisaged but the deployment of meshed HVDC offshore grids is currently hindered by the high cost of converter technology, lack of experience with protection systems and fault clearance components and immature international regulations and financial instruments. PROMOTioN will overcome these barriers by development and demonstration of three key technologies, a regulatory and financial framework and an offshore grid deployment plan for 2020 and beyond. Note: TRLs for this project have not been updated. | http://cordis.europa.eu/project/rcn/199016_en.html | 2019 | 2021
Enabling technologies for HV DC Grids
500kVdc+ cable testing | Innovation Area | TRL 3 | TRL 5 | Academia | Owner Operators | Enabling disruptive innovation | Beyond 500kV+ HVDC Cable Test Methodology. Even though there are commercialised cables rated 525Kv, there is no representative testing method (currently use overhead cabling method) |  | 2019 | 2033 | M | L | M | n/a
DC-DC HV Transformer | Innovation Area | TRL 4 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Enabling disruptive innovation | Looking into multi-terminal DC Grids - Development and demonstration of HV DC:DC Convertor including high frequency power transformer |  | 2019 | 2028 | M | L | M | L |  |  |  | Slightly reduced weight and size of turbine
DC-DC MV Transformer | Innovation Area | TRL 4 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Enabling disruptive innovation | Looking into multi-terminal DC Grids - Development and demonstration of MV DC:DC Convertor including high frequency power transformer |  | 2019 | 2023 | M | L | M | L |  |  |  | Slightly reduced weight and size of turbine
Offshore DC Circuit Breaker and Protection | Innovation Area | TRL 7 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Development of fast responding breaker and protection technologies used in offshore wind HVDC transmission. |  | 2019 | 2023 | M | M | M | L |  |  |  | Small impact on H&S due to less rush for marine operations to repair the cable
Enabling Research
Digitalisation and Information Systems
Artificial Intelligence | Innovation Area | TRL 1 | TRL 6 | Academia | Owner Operators | Enabling disruptive innovation | Artificial Intelligence can have multiple applications in all stages of windfarm lifecycle. Taking O&M as an example – AI application involves a supervisory system that utilises conventional design and operation rules combined with Machine Learning/Deep learning from big data from the internet of things. AI could be a decision support system or a complete framework for collecting information and acting upon this without human intervention. Challenges are verification/validation of AI systems and quantitative assessment of confidence in AI performance. Other examples could include design optimisation, turbine control, Turbine Yaw Error and Control, Grid Balancing or Transmission Fault Diagnostics and Prognostics. |  | 2019 | 2035 | H | M | M | H
Data utilisation | Innovation Area | TRL 3 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Data utilisation is an overarching term used to describe a wide range of concepts and techniques aimed at exploiting available information. In this context data utilisation is performed with the aim of data-driven decision making. In the offshore renewables Industry/SMEs, data utilisation techniques can include: post-event analysis, use of current operational data and forecasting of future trends. The level of data utilisation is varied across Industry/SMEs, providing the opportunity for innovation and collaboration between offshore wind stakeholders. |  | 2019 | 2030 | M | M | M | L | This depends on the engagement by OOs and the impact their use of data has. | UK has high expertise in this field and can actively engage in data and digital activities. | Although some OOs do actively engage in data utilisation activities, some will need external bodies to help kickstart a culture change within their organisation. | Optimised O&M operations
Internet of things | Innovation Area | TRL 3 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Internet of Things involves an increased level of interaction and communication between measurement systems and components being monitored. it is seen as an evolution to current capabilities of condition and health monitoring technologies. Major challenges include reliability and calibration of sensor systems as well as security and access to information. There is requirement of coordination of work between RTOs, Academia and Industry/SMEs. |  | 2019 | 2030 | M | M | H | L | This will involve system integration of SCADA and SHM systems | Unlikely to involve protected IP, more likely to result in communications protocols and standards/best practice.
Machine learning | Innovation Area | TRL 3 | TRL 6 | Academia | Owner Operators | Enabling disruptive innovation | Make use of machine learning applications and draw benefit from disparate data sources to optimise OWF operation strategies. Challenges to be addressed when making use of machine learning applications include the integration and validation of numerical models with sensor data to come up with accurate interpretation or diagnostics of phenomena or activities of interest. |  | 2019 | 2025 | M | H | H | M |  | Potentially an area where the UK can be a real leader |  | Optimised O&M operations
Design and materials
Design for marine life and aquaculture | Innovation Area | TRL 2 | TRL 5 | Academia | Owner Operators | Enabling disruptive innovation | Currently, the design process of a turbine, an array and associated infrastructure does not take into account the potential to enhance marine life (biodiversity), contribute to fisheries sustainability or aquaculture production. This process may have conservation value and may provide nursery areas for commercially relevant fish and shellfish, but there is a need to undertake research to assess the potential value of this process. In the longer term, this could contribute to the sustainability of local fishing opportunities. The use of offshore renewable sites for aquaculture has been explored in principle and through some limited trials, but there are likely to be significant logistical, biological and economic challenges to successful, commercial deployment. There is opposition to renewables developments that are perceived or in reality compromise fishing activity. Developing clear and demonstrable pathways to achieving these objectives could potentially help to streamline consenting and licencing processes and perhaps more importantly secure social license. There are potentially significant cost savings in this process. |  | 2019 | 2030 | L | M | M | H |  | This element wouldn’t drive LCOE down but could enable additional revenue generation. Successful design could boost fishing Industry/SMEs confidence to go back to fishing grounds. | Links to sustaining a strong commercial fishing Industry/SMEs
Innovation in design concepts | Innovation Area | TRL 1 | TRL 4 | Academia | Owner Operators | Enabling disruptive innovation | Explore how potential large arrays located far from shore farms (wind, tidal and wave) might lead to different optimal design concepts than those already adopted. |  | 2019 | 2033 | M | H | H | M |  | Totally new design concept could be developed and UK could export knowhow, R&D and potentially manufacture of new-concept turbines. | Due to the low TRL, this must be driven by academia, but the participation of Industry/SMEs is critical to assure significance and relevance of the proposed concepts. | Results are unknown yet as it will depend on a design
Self-healing materials | Innovation Area | TRL 3 | TRL 5 | Academia | Original Equipment Manufacturers | Enabling disruptive innovation | Development of materials that can maintain their integrity and self-heal when deficiencies occur due to material degradation. Materials could be applicable to any asset that's exposed to environmental conditions: blades, tower, substructures, cables. In electrical infrastructure power cable failure in wet environments arises most frequently from damage to the protective sheath or jacket layers allowing rapid water ingress. |  | 2019 | 2035 | H | H | M | L |  |  |  | May reduce number of minor repairs
CableCare 2: Self-repair Subsea Cable Demonstrator | Ongoing R&D project | TRL 1 | TRL 1 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Power cable failure in wet environments arises most frequently from damage to the protective sheath or jacket layers allowing rapid water ingress. This is preventable by inclusion of a water blocking material within the cable assembly, although existing solutions suffer from poor performance and added cost due to incompatibility with standard power cable production processes. CableCare2 harnesses the laboratory validated water blocking capabilities of a water swell-responsive polymer blend, which consequently self-repairs to prevent water penetration and to block permeation of any water present, promising major improvements in mitigating cable failure. The material process characteristics align with current cable co-extrusion techniques, to be deployed as a subsheath repair layer and inner water blocking protection. Note: TRLs for this project have not been updated. | https://gtr.ukri.org/projects?ref=104361 | 2019 | 2021