## Version Control
Document name | Electrical Infrastructure Innovation Roadmap
Document Number | PN000384-ANA-004
Issue Number | 8
Issue No: | Date Issued: | Author | Approver | Revision History
1 | 2018-02-28 | K. Stefaniak | J. Flowers | First Issued
2 | 2018-10-25 | K. Stefaniak | A. Stormonth-Darling | Second Issued
3 | 2019-04-05 | K. Stefaniak | A. Stormonth-Darling | Third Issued
4 | 2020-01-31 | K. Stefaniak | A. Stormonth-Darling | Fourth issued
5 | 2020-09-30 | K. Stefaniak | A. Stormonth-Darling | Fifth issued
6 | 2021-01-21 | K. Stefaniak | A. Stormonth-Darling | Sixth Issued
7 | 2021-08-20 | C. Wilson | K. Stefaniak | Seventh Issued
8 | 2022-04-08 | C. Wilson | K. Stefaniak | Eighth Issued
Disclaimer Notice
Whilst the information contained in this report has been prepared and collated in good faith. The Offshore Wind Innovation Hub makes no representation or warranty (express or implied) as to the accuracy or completeness of the information contained herein nor shall we be liable for any loss or damage resultant from reliance on same.

## Electrical Infrastructure
Description | Type of Entry | Requires Implementation Offshore | Start TRL | Target TRL | Enabler | Beneficiary | Strategic Outcome | Notes | Website | Forecast Start | Forecast Finish | Potential to Reduce LCoE | UK Benefit | Case for Intervention | HSE Impact | Potential to Reduce LCoE (comments) | UK Benefit (comments) | Case for Intervention (comments) | HSE impact (comments)
Electrical Infrastructure
Component Reliability Improvement
Cables
Improved standards of cables | Innovation Area | NO | TRL 7 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising>15MW turbine platforms | Background: As the amount and length of installed submarine cables increases, the need to optimise designs, testing and certification techniques increases as well. With new cable systems coming to the market still on a regular basis, continued industry innovation support is required. Innovation: Seek improvement of offshore wind subsea power cables standards including all types of pre-commercial and factory testing. Standards are still sup-optimal and e.g. implications of marine growth have to be understood better. |  | 2022 | 2038 | H | M | H | L |  | Numerous projects in the UK attempting to tackle this issue |  | Improved design would lead to less failures and decreased frequency of underwater inspection
Better insight of root cause of cables failures | Innovation Area | NO | TRL 5 | TRL 7 | Catapult | Owner Operators | Commercialising>15MW turbine platforms | Background: As the amount and length of installed submarine cables increase the need to optimise designs, testing and certification techniques increases as well. With new cable systems coming to the market still on a regular basis, continued industry innovation support is required. Innovation: Better understanding of loading conditions, fault location and failure modes of subsea power cables. Possible solution includes use of data driven anomalies or fault identification. |  | 2022 | 2025 | H | M | M | n/a
Representative accelerated testing of cables | Innovation Area | NO | TRL 5 | TRL 9 | Catapult | Owner Operators | Commercialising>15MW turbine platforms | Background: As the amount and length of installed submarine cables increase the need to optimise designs, testing and certification techniques increases as well. With new cable systems coming to the market still on a regular basis, continued industry innovation support is required. Innovation: Develop more representative cable testing methodologies to better understand failure mechanisms (e.g. better representation of loading conditions with simultaneous electrical and mechanical stress) and recommend mitigation measures and solutions. |  | 2022 | 2025 | H | M | H | n/a
Lead-free HV inter-array cables (132kV+) | Innovation Area | YES | TRL 3 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Commercialising>15MW turbine platforms | Background: At present offshore wind farm dynamic cables operate up to 66kV. At this voltage level lead sheaths are not required. However, cables above 66kV will require the water blocking features offered by lead sheaths to prevent water ingress to the conductor. Because of this requirement, it stands as a major barrier to dynamic cables rated above 66kV, with offshore transmission voltages above 66kV being highly necessary to accommodate higher turbine ratings of 20MW+ in the future. Innovation: Research is required to find suitable replacements to lead sheaths that maintain the same level of water blocking ability. Efforts required here include the need to develop a cable which can be demonstrated at scale to push TRL closer to large-scale commercialisation. |  | 2022 | 2027 | M | H | M | H | Larger quantities of power can be generated via higher voltage levels, also resulting in lower transmission losses. | JDR set to lead the way with dynamic cables above 66kV. High export potential for the UK. | Medium-Low. JDR received BEIS funding but this innovation is one which would gradually make way to market without additional funding.
Electrode (Electrical Cable Failure Trending & Reliability Analysis for Operational Developments) | Ongoing R&D project | NO | TRL 1 | TRL 1 | Catapult | Owner Operators | Commercialising>15MW turbine platforms | ELECTRODE is the first programme of its kind for the continuous collection of anonymous data around subsea cable failures in offshore wind. The new platform, to be launched by ORE Catapult early in 2021, will track failures, service downtime, as well as the effectiveness of the repair and monitoring procedures, and use of technology in cable failures. Subsea cable failures are the biggest insurance cost for the industry, accounting for 75-80 per cent of claims in the UK. The cost implications of even a single cable failure can be enormous too, taking an average of two months to repair and often exceeding the £10 million mark in costs and lost power generation. ELECTRODE (Electrical Cable Failure and Reliability Trending for Operational Developments) will involve collaboration and the continuous collection of anonymous data, paving the way for radical advancements in the offshore wind industry. It will be operated in a similar way to our SPARTA model, with anonymity the core principle of the platform. There will be no risk to owner/operators who take part. | https://ore.catapult.org.uk/stories/electrode/ | 2022 | 2025
Components
Development of components health monitoring | Innovation Area | NO | TRL 4 | TRL 9 | Research Technical Organisations | Owner Operators | Enabling disruptive innovation | Background: Condition monitoring (CM) system has been developed for individual component inside a turbine. There is no holistic CM platform to host all individual component level CM systems, share component conditions and optimise monitoring performance. Innovation: Integration of electrical infrastructure component condition-based health monitoring (CBHM) into a single intelligent platform along with other CM system could be new solutions to develop, which will interchange the information and improve the CM results. For example, development of integrated power quality or converter power electronic monitoring within the turbine control. Relatively new area, with big SMEs opportunities. |  | 2022 | 2025 | M | M | M | M | Reduced OPEX. | UK-based academia and RTO are well placed to develop methodologies and verify these. | It will be limited by the available turbine OEM in the UK. | Decreased number and scale of marine operations
Demonstration of components health monitoring | Innovation Area | NO | TRL 5 | TRL 9 | Industry/SMEs | Owner Operators | Maximising operational performance of existing wind farms | Background: Condition monitoring (CM) system has been developed for individual component inside a turbine. There is no holistic CM platform to host all individual component level CM systems, share component conditions and optimise monitoring performance. Innovation: Integration of electrical infrastructure component condition-based health monitoring (CBHM) into a single intelligent platform along with other CM system could be new solutions to develop, which will interchange the information and improve the CM results. For example, development of integrated power quality or converter power electronic monitoring within the turbine control. Relatively new area, with big SMEs opportunities. |  | 2022 | 2028 | M | M | M | M | Reduced OPEX. | Big data driven approach will be under development, collaborating AI companies in UK with turbine operational data. There is an increasing number of UK data companies involved in maintenance business. | Big data technology provides an opportunity to monitor the health condition from a way different from turbine OEM, which could generate new patent and innovate the O&M | Decreased number and scale of marine operations
Subsea connectors | Innovation Area | YES | TRL 5 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Subsea cable connector is a key contributor to subsea cable repair. Usually, it is provided by the corresponding wind farm export cable manufacturer. Once cable fault happens, it takes time to coordinate necessary repair with the manufacturer and financial losses rise due to cable downtime. Innovation: Universal subsea connectors will greatly reduce the cost of itself, improve the cable repair efficiency and reduce wind farm downtime. Sector such as Tidal and Wave can benefit from improved design solutions, and demonstration these in a representative environment. |  | 2022 | 2030 | L | M | L | M | Universal subsea connectors will standardise the design and reduce the cost | Leading transmission cable manufacturers are outside the UK | New IP in subsea transmission cable installation and condition monitoring | Designed to reduce environmental impact
Future Internal Array Systems
66kV+ Cables & Components | Innovation Area | YES | TRL 5 | TRL 7 | Research Technical Organisations | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Background: Moving to 66 kV has been seen as a significant step forward in reducing windfarm costs. However, with turbine ratings continuing to grow and further cost reductions necessary higher interarray voltages will be needed in the near future. Innovation: Interarray voltages greater than 66kV. Higher voltage cables, circuit breakers and switchgear are required within the tight spaces available offshore and must be capable of withstanding the harsh environments that offshore windfarms experience |  | 2022 | 2024 | M | L | H | L
Flexible Offshore Wind Solutions
Energy storage
Turbine level storage | Innovation Area | YES | TRL 4 | TRL 7 | Research Technical Organisations | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | The electricity grid is changing with higher penetration of renewable energy and offshore wind becoming a large part of the future energy mix. As offshore wind penetration increases, older large generation power plants are gradually been phased off. These come with some challenges as the inertia capability these plants provide is reduced leading to instability and transients in the electricity grid. Generation plants are also known to provide black starting capabilities to re-energise the grid when there’s a black out and new solutions are envisaged around windfarms to provide this service in the future. Turbine level storage is a way forward and can support the grid by providing to provide synthetic inertia through virtual synchronous generator operation with energy storage embedded at turbine platform. Energy Storage would also provide the grid forming capabilities required under black starting operation. This would also increase the lifetime of turbine components and the amount of energy integrated into a grid. The biggest challenge in this area is to produce simulation modelling and demonstration capabilities. These solutions can also applicable into wave & tidal devices. |  | 2022 | 2023 | M | M | L | M |  |  |  | Turbines would be more reliable and wouldn’t require urgent marine operations if it loses connection to the grid.
Windfarm co-located electricity storage systems | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | The intermittent nature of wind limits the capability of generating power from wind turbines and power generated often is curtailed to meet the demand. Electricity storage systems co-located around wind turbines and farms provide more operation flexibility reducing the need for curtailment as excess generation in low peak demand period can be stored and dispatched during high peak demand periods. Electricity storage systems could also potentially assist the development of innovative solutions around providing ancillary services for grid with wind turbines and farms. The major challenge is a better understanding of how these can be deployed on a large scale with wind farms. Other issues to address include integration, grid support and voltage/frequency requirements and the optimal strategic locations to deploy this within the existing electrical infrastructure. Pilot projects around demonstration of on/offshore energy storage for wind farms will be necessary to find answers |  | 2022 | 2025 | H | M | M | L
Big scale energy storage, e.g. hydrogen | Innovation Area | YES | TRL 5 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Industry’s ambition is to reach 40GW capacity by 2030. In order to achieve this goal, most of the energy supply will have to be carbon neutral and renewable. The move towards a sustainable pathway by decarbonising the future energy system will depend on the ability to store and transport energy in an efficient and cost-effective way. Big scale energy storage through production of hydrogen is versatile and offers a way to decarbonise a range of sectors including transportation, oil and gas, chemicals, heating and power for buildings and renewable power generation. The potential for offshore wind in the hydrogen transformation is huge with the vast amount of wind energy that be converted to hydrogen and stored to provide a service to different sectors. Hydrogen is almost entirely supplied from natural gas and coal today and producing hydrogen from low-carbon energy is costly at the moment. The development of hydrogen infrastructure is slow and holding back widespread adoption with regulations currently limiting the development of a clean hydrogen industry. Further commercialisation work is needed to other to achieve large scale productions and feasibility and pilot studies on building hydrogen infrastructure required for this transformation is required. |  | 2022 | 2027 | H | H | H | L
Hybrid synchronous compensator | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Synchronous compensators are a mature technology in the electricity grid that has been used to provide reactive power and voltage support. A hybrid synchronous compensator which couples the benefits of energy storage in addition with Static Compensators STATCOMs could provide additional support and provide a variety of ancillary services to the grid. A challenge in this area is understanding how best to utilise an optimise the usage of this technology within the existing offshore wind electrical infrastructure. |  | 2022 | 2025 | M | M | L | n/a
Cross-sector renewable integration
Repurposing O&G platforms | Innovation Area | YES | TRL 4 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Background: The UK has significant wind power potential, untapped carbon storage capacity (CCS), and extensive oil and gas infrastructure in place. Platform electrification and gas-to-wire are mature and can enable near-term oil and gas industry emissions reductions, but there are cost challenges. Innovation: Abandoned or old O&G platforms to be decommissioned could be converted into production and storage units that convert electricity from OSW farms into hydrogen and synthetic gas. The repurposing could transition over time from Electrification, Gas to wire, CCS, Blue hydrogen, Green hydrogen, Large scale energy hubs. |  | 2022 | 2030 | M | M | M | M | Re-purposing O&G platforms could provide a commercial steppingstone for green hydrogen production. Also, many existing structures could be operated for another 30/50 years - cost benefits over installing completely new infrastructure. | Reduces / delays decommissioning liabilities for O&G Operators. Platforms likely to be well located for new energy hubs
Offshore green hydrogen production | Innovation Area | YES | TRL 4 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Background: The move towards a sustainable pathway by decarbonising the future energy system will depend on the ability to store and transport energy in an efficient and cost-effective way. One of possible solutions to decarbonise the economy is green hydrogen usage. At present, hydrogen is almost entirely supplied from natural gas and coal, with green hydrogen production from excess renewable electricity generation being costly at the moment. Innovation: For a route towards large-scale green hydrogen production regulatory intervention is needed to mature the hydrogen market so that numerous hydrogen related innovations can be pushed forward. |  | 2022 | 2030 | H | H | H | n/a | Hydrogen is cheaper than batteries for large-scale storage and is less geographically dependant than pumped hydro/compressed air and therefore more scalable. Estimated to be most cost effective than fossil fuels for transport in the long-run, and is already cheaper than electric heating. | Green offshore hydrogen is the most cost-effective when produced from offshore wind and it also allows repurposing of existing O&G assets. | Big industry players already investing and developing H2 technologies, both in renewable and O&G sector, but public support for large scale demonstrators is necessary. Intervention will be required in regulations, e.g. blending H2 into UK gas grid. | May actually increase H&S risk initially.
O&G platform electrification | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Electricity consumption of offshore oil and gas rigs are commonly supplied by gas turbines located on the platforms. These are expensive to operate and emit significant amounts of CO2 and NOx. Offshore wind farms can be an economic and environmentally sound option for supplying electricity to oil and gas rigs. This may include floating wind solutions, interconnection of offshore wind and O&G assets and/or powering platforms from shore. |  | 2022 | 2025 | M | H | M | M |  |  | Strong drive to optimise the use of UKCS for multiple user coexistence | O&G H&S procedures possibly more demanding
Gas to Wire | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Background: The gas-to-wire (GTW) concept refers to the burning of gas offshore with the electricity transmitted to shore via subsea cable. Existing hubs could be fully converted (such that all gas produced would be converted to power) or partially converted e.g. power generated from an offshore GTW facility would be routed to shore via the export cable installed for the nearby offshore windfarms. As a relatively flexible and fast responding form of power generation, it could play a useful role in balancing the electricity grid as supply and demand fluctuates. Innovation: Whilst individual elements of offshore GTW are already proven separately (e.g. offshore gas production, gas-fired power generation, subsea power transmission), the overall concept is yet to be commercialised and a full demonstration is required. It is a niche solution although might be attractive for Southern North Sea (SNS) and East Irish Sea (EIS). |  | 2022 | 2025 | H | H | M | L |  |  | Strong drive to optimise the use of UKCS for multiple user coexistence | O&G H&S procedures possibly more demanding
Ocean-REFuel - Ocean Renewable Energy Fuels | Ongoing R&D project | YES | TRL 1 | TRL 1 | Academia | Other Suppliers | Enabling disruptive innovation | Background: Ocean-REFuel was established investigate low pressure solutions to store hydrogen in much smaller volumes safely using solid state storage. Also, to maximise hydrogen system efficiency by developing low energy solid state compressors. They will also implement a techno-economic assessment of proposed solutions, assessment of the circular economy for the new technologies and the integration and potential impact of ocean net-zero fuels on the existing gas network infrastructure. | https://gtr.ukri.org/projects?ref=EP%2FW005158%2F1 | 2022 | 2026
High efficiency reversible solid oxide cells for the integration of offshore renewable energy using hydrogen | Ongoing R&D project | YES | TRL 1 | TRL 1 | Academia | Owner Operators | Enabling disruptive innovation | The production, storage, distribution and conversion of hydrogen is a rapidly emerging candidate to help decarbonise the economy. Focus is needed on its integration with offshore renewable energy (ORE), a topic of increasing importance to the UK given the falling costs of offshore wind generation (with prices expected to drop to 25% of 2017 by 2023) and Government ambition. Indeed, the latest BEIS scenarios include more than 120 GW of offshore wind, and even up to 233GW in some scenarios. This brings with it significant challenges to the electricity infrastructure in terms of our ability to on-shore and integrate these variable energy flows, across a wide range of timeframes. Much of the focus of these national strategies is on the production of 'green' hydrogen using electrolysis, driven by renewable electricity. However, there remains interest in some countries, the UK being one example, in 'blue' hydrogen, which is hydrogen made from fossil fuels coupled with carbon capture and storage and hence a low carbon rather than zero carbon hydrogen. Today, 96% of hydrogen globally is produced from unabated fossil fuels, with 6% of global natural gas, and 2% of coal, consumption going to hydrogen production, primarily for petrochemicals, contributing around 830 million tonnes of carbon dioxide emissions per year. Currently green hydrogen is the most expensive form of hydrogen, with around 60-80% of the cost coming from the cost of the electrical power input. A critical factor that influences this is the efficiency of the electrolyser itself, and in turn the generator used to convert the green hydrogen back into power when needed. In this work we focus on the concept of a reversible electrolyser, which is a single machine that can both produce power in fuel cell mode, and produce hydrogen in electrolyser mode. Electrolysers and fuel cells fall into one of two categories: low-temperature (70-120C) and high temperature (600-850C). While low temperature electrolyser and fuel cell systems are already commercially available, their relatively low combined round-trip efficiency (around 40%) means that the reversible solid oxide cell (rSOC), which can operate at high temperatures (600-900C) is of growing interest. It can achieve an electrolyser efficiency of up to 95%, power generation efficiency of up to 65%, and hence a round-trip efficiency of around 60% at ambient pressure using products now approaching commercial availability. This project considers the development and application of this new technology to the case of ORE integration using hydrogen. | https://gtr.ukri.org/projects?ref=EP%2FW003686%2F1 | 2022 | 2025
Alternative Grid Solutions
Alternatives to Grid
Supergrid | Innovation Area | YES | TRL 7 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | A super grid is a large electrical network (grid) that crosses national borders. The system intends to use HVDC technology to transmit electrical power long distances. The concept would change the way energy was transmitted cross-country running predominately on renewable energy (for example offshore wind farms). Renewable energy is an intermittent source of generation which can cause challenges for the electrical network’s stability. The concept of a supergrid can potentially counteract this problem of intermittency due to the flexibility of such a large electrical system allowing the network to run primarily on renewables. Multiple countries could benefit from resources that they wouldn’t generally have access to. For example, the wind resource in the North Sea could benefit further away locations (Spain / Portugal). Supergrid could provide better energy security, decentralisation, better electrical trading and has potential to completely remove fossil fuel electrical generation from the grid and enable better cross-country energy trading. |  | 2022 | 2040 | H | H | H | L | Due to the potential flexibility of the system, cross border trade and the increase in offshore wind development the LCoE is expected to fall. | Supergrid would remove installed capacity limit and enable UK to increase energy trade through interconnectors. It would also significantly improve European security of supply. | The UK will need to be involved with the vast wind farm development in the North Sea. The innovation area will continue to progress but there are many enablers and beneficiaries involved which require coordination. | The supergrid would contribute to reducing the energy sectors environmental impact.
Low Frequency AC Transmission | Innovation Area | YES | TRL 5 | TRL 7 | Research Technical Organisations | Owner Operators | Enabling disruptive innovation | Background: Low Frequency AC (LFAC) transmission at 16.7 Hz is considered as potentially an optimum solution for the interconnection of offshore wind for power transmission distances in the 80‐200 km range. LFAC individual system components are in existence in the railway industry but currently no system integration has been implemented for LFAC in the transmission system for the connection of remote islands or offshore wind farms. It could potentially help reduce the cost of transmission for offshore wind developers improve the efficiency of transmission. Innovation: Existing challenges include AC equipment dimensioning and wind turbine operation in low frequency grids. It would require new testing methods, standards and general regulatory framework. It could also have implications on the design of the turbine. However, the industry has focused on developing HVDC transmission technology and LFAC might take more time (if ever) to commercialise. |  | 2022 | 2030 | M | M | M | n/a | Some reports (112843-UKBR-R-01-F) point out there could be a potential significant cost reduction if low frequency AC is used |  | The outcome of the new offshore HVDC projects currently under development may have a significant impact on the pursue of LFAC transmission
Hydrogen Transmission | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Background: The move towards decarbonising the wider energy system will depend on the ability to store and transport energy in an efficient and cost-effective way. One of possible solutions to decarbonise the economy is green hydrogen usage. However, the infrastructure to transport is currently highly underdeveloped. Innovation: For a route towards suitable hydrogen transmission infrastructure regulatory intervention is needed to mature the hydrogen market so that numerous innovations can be pushed forward. |  | 2022 | 2030 | M | H | H | L | Development of transmission network for hydrogen would allow more hydrogen to be used for heating, transport, and energy storage for the grid. Although not all of these are cost-competitive with conventional methods, the price will come down and has the potential to be cheaper than existing energy sources | Green offshore hydrogen is the most cost-effective when produced from offshore wind and it also allows repurposing of existing O&G assets. | Big industry players already investing and developing H2 technologies. Intervention is needed on the policy side from government to allow hydrogen blending into the gas network. | As the majority of the hydrogen transmission network will be repurposed or upgraded existing pipelines, and with gas transmission being a well-known and mature technology within the O&G sector, the HSE impact will likely be minimal. Hydrogen leakage is usually less dangerous than natural gas as it easily escapes into the atmosphere rather than pooling. Work is being done on improving odorant additives to help detect hydrogen leakages.
Grid flexibility
Smart Power Networks | Innovation Area | NO | TRL 6 | TRL 8 | Research Technical Organisations | Owner Operators | Maximising operational performance of existing wind farms | Background: Optimising the utilisation of new and existing offshore wind electrical control systems would provide a more efficient means of maximising generation, reducing losses, and improving the operational control of offshore wind farms. Network automation solutions combined with clever co-ordination between the wind turbines, farms controllers and wider active management systems will optimise the operation for services provided to the electricity grid. This will span across solutions covering cyber security, data prognosis and diagnostics through IoT cloud computing, virtual private wires, islanded local microgrids, generator and load active management systems, and local energy markets. These can prove to be the solutions for a smarter and more efficient power network for offshore wind turbines and farms. Innovation: Gaining a greater understanding of such programmes would foster new business models and commercial arrangements. Cyber security solutions can be explored under existing and new security frameworks for offshore wind, and network automaton can be deployed through pilot projects for different applications. However, regulatory intervention is required to accommodate new business models which will push many of these innovations forward. |  | 2022 | 2025 | M | M | H | L | Medium-High
Ancillary Services: Frequency Support | Innovation Area | NO | TRL 5 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising>15MW turbine platforms | Background: Offshore wind and other low marginal cost generation technologies are inflexible in response to market signals. The increasing penetration of converter-connected generation is reducing system inertia, increasing the level of available response required. Innovation: There is research needed in how project developers and owners can directly change their generation characteristics, and thus their impact on the grid. Owner operators are neither encouraged nor penalised to balance the grid. Ancillary service revenue mechanisms need to be considered via grid regulation changes so that turbines and offshore infrastructure can contribute to onshore frequency stability. Ancillary services have the potential to be of huge financial benefit as well as playing a role in reducing LCOE, but this depends on how extra revenue obtained from future ancillary services are calculated. |  | 2022 | 2025 | L | H | H | n/a | The requirement to provide frequency support may come via connection requirement
Ancillary Services: Inertia Support and Blackstart | Innovation Area | NO | TRL 6 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising>15MW turbine platforms | Background: Moving away from traditional means of generation from fossil fuels power plants to offshore wind comes with the risk reducing system inertia. This is resulting in increased grid sensitivity levels which can lead to partial or full system blackout. In the past, means of providing the service of restarting and re-energising the electricity grid was through coal powered black start generators. This is now changing, and in the future, this will be provided by a mix of generators including offshore wind. Innovation: There is research needed in how offshore wind can be part this mix and how its impact on the grid can improve system inertia with the ability to provide black start support. Ancillary services have the potential to be of huge financial benefit as well as playing a role in reducing LCOE, but this depends on how extra revenue obtained from future ancillary services are calculated. |  | 2022 | 2025 | M | H | H | n/a
Enabling technologies for HV DC Grids
DC-DC MV Transformer | Innovation Area | YES | TRL 4 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Using DC, power can be transferred over longer distances without the need for an offshore substation. Looking into multi-terminal DC Grids - Development and demonstration of MV DC:DC Convertor including high frequency power transformer. These could be placed in the turbine tower/nacelle and connected directly to an MVDC grid. Innovation: Work is required to permit high voltage terminations within the confined space of an offshore turbine. |  | 2022 | 2025 | M | L | M | L |  |  |  | Slightly reduced weight and size of turbine
DC-DC HV Transformer | Innovation Area | YES | TRL 4 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Using DC, power can be transferred over longer distances without the need for an offshore substation. Looking into multi-terminal DC Grids - Development and demonstration of HV DC:DC Convertor including high frequency power transformer. These could be placed in the turbine tower/nacelle and connected directly to an MVDC grid. This would be a necessary step for HVDC Integration. Innovation: Work is required to permit high voltage terminations within the confined space of an offshore turbine. |  | 2022 | 2030 | M | L | M | L |  |  |  | Slightly reduced weight and size of turbine
500kVdc+ cable testing | Innovation Area | NO | TRL 3 | TRL 5 | Academia | Owner Operators | Enabling disruptive innovation | Background: Cable failures is an ongoing issue in offshore wind industry. There is no representative testing methodology for offshore cables, including beyond 500kV+ HVDC cables. Even though there are commercialised cables rated 525Kv, there is no representative testing method (currently use overhead cabling method). Innovation: Development of a representative test methodology for 500kV+ HVDC cables. |  | 2022 | 2035 | M | L | M | n/a
Superconducting Cables | Innovation Area | YES | TRL 5 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising>15MW turbine platforms | Superconducting cables have been around longer than most realise. There have been some successful land-based demonstration projects. However, it has not made it into the mainstream offshore wind industry. The biggest benefit is the dramatic reduction in resistive losses. However, these cables are more complicated in their nature. |  | 2022 | 2040 | M | M | H | L | Cable costs are a significant driver in the CAPEX and OPEX costs of the wind farm. Such cables could reduce the amount of copper required and dramatically reduce the operational losses. | As such technology is still largely yet to be exploited commercially for offshore wind there is the opportunity for UK companies to seize the market here. | The concept has been around for quite some time but is yet to get a serious foothold in the industry. Confidence is required.
DC networks, power quality and plant reliability | Ongoing R&D project | NO | TRL 1 | TRL 1 | Academia | Owner Operators | Enabling disruptive innovation | The movement of electrical energy from generators to customers, through electricity networks, has historically been based on High Voltage Alternating Current (HVAC) technology. This has been a major success of the twentieth century, enabling reliable and stable energy supplies across the developed world. The technology dominated partly as a result of the ability to change voltage levels readily and efficiently using transformers. The alternative technology of High Voltage Direct Current (HVDC) has historically only been used for point-to-point links because of particular advantages in this situation. Now however, with the advent of power electronics, utilisation of HVDC systems is rapidly increasing across the world. This has been accelerated with the growth of renewable distributed energy supplies, such as offshore wind farms in the UK. As a result, local and international energy supplies are becoming dependent on HVDC. Consequently, the reliability of DC technologies is becoming critical as they become more embedded in supply networks. However, in comparison to AC systems, the understanding of insulation and plant reliability under HVDC is still in its infancy. At the same time, the working environment for DC plant is not well documented and, in reality, DC systems have AC ripple, impulses and voltage variation just as in any other system, and these time-varying waveforms are likely to control plant ageing and reliability. This project comprises internationally leading researchers from The University of Manchester, The University of Strathclyde and Imperial College. They bring complementary expertise to form a unique team to address the problem. Prof Tim Green (Imperial) is an expert in the use of power electronics to enhance the controllability and flexibility of electricity networks; Prof Simon Rowland (Manchester) is an authority on ageing of high voltage insulation materials; and Prof Brian Steward (Strathclyde) has unique experience in condition monitoring and insulation diagnostics for high voltage systems. The project is designed to embed the work into the global community and in particular is linked to researchers in China where the largest systems are being developed. Through these means we hope to de-risk the UK's growing dependence on DC networks, and optimise equipment and system design and operation. Note: TRLs for this project have not been updated. | https://gtr.ukri.org/projects?ref=EP%2FT001232%2F1 | 2022 | 2023
Floating Wind
Improvements in AC dynamic cables | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Dynamic 66kVAC cables are used for the floating wind turbine array cable. Due to the floating platform, the wind turbine export cable will suffer stresses from wind, wave and current. Currently, the cable failure mechanism, interface with static cables and interface with a substructure are not well understood and O&G standards are used. Innovation: It requires aerodynamic, hydrodynamic, material and electrical background to investigate the cable failure and achieve a better reliability of the cable. Once design mechanisms are understood and fit for offshore wind purpose, cables should be standardised to allow manufacturing and maintenance at a lower cost. |  | 2022 | 2035 | H | M | H | n/a | Full-size test result can help design digital modelling and improve its accuracy, saving the design cost and time in future |  | Full-size test result can help design digital modelling and improve its accuracy, saving the design cost and time in future
Improvements in HVDC dynamic cables | Innovation Area | YES | TRL 3 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Dynamic HVDC cables do not currently exist. For far offshore wind farms in deeper water requiring floating substations, this is a key enabling technology as the export cable will suffer stresses from wind, wave and current. Currently, the cable failure mechanism, interface with static cables and interface with a substructure are not well understood and O&G standards are used. Innovation: It requires aerodynamic, hydrodynamic, material and electrical background to investigate the cable failure and achieve a better reliability of the cable. Once design mechanisms are understood and fit for offshore wind purpose, cables should be standardised to allow manufacturing and maintenance at a lower cost. |  | 2022 | 2035 | M | L | M | n/a | Allows floating substations in deep water which may be cheaper than building very large structures or creating a submerged substation. | Low as there is limited export cable design and manufacture activities in the UK. Also, water depth in the UK is likely to lead to relatively few locations where floating HVDC would be used. | While not directly applicable to the UK industry, there is the opportunity to export knowledge to the East and USA where the technology will be more used. The design of such cables requires input from multiple different sources and secrecy will lead to compromised designs and delay deployment. For example, knowledge of failure mechanisms leads to effective monitoring platforms reducing maintenance costs
Design of electrical components to withstand floating wind conditions | Innovation Area | YES | TRL 5 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Background: The electrical infrastructure for floating wind components needs to resist the motions of the hull, both in terms of extreme motions and fatigue over the lifetime of the project. Additionally, floating platform substation will have to include loads resistance for low frequency, high acceleration events and larger number of fatigue cycles over its lifetime. Innovation: The design of power converter, transformer, circuit breaker etc. should include these conditions for floating wind application. |  | 2022 | 2029 | L | L | M | L | Potential to reduce OPEX costs and reduce lost power production. |  | This work to be led by equipment OEMs due to IP considerations. Classification societies will need to be involved to certify that new product meets the requirements of floating wind. | Reduced requirement for repairs leading to improved H&S. Some electrical components utilise very environmentally unfriendly gasses. There is a potential to reduce the probability of equipment failure and leakage of these gasses.
Design of floating platform substation | Innovation Area | YES | TRL 4 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Background: The water depth or seabed conditions are prohibitive to have bottom-fixed substation in some cases and floating platform will have to be used. The equipment needs to resist the motions of the hull, both in terms of extreme motions and fatigue over the lifetime of the project. Designs of floating platform substation will have to include loads resistance for low frequency, high acceleration events and larger number of fatigue cycles over its lifetime. Innovation: Even though there are no major barriers to feasibility and existing technology is largely considered to be suitable, it will require some modifications to give relatively small maximum accelerations. Some designs are already in the market but require further optimisation and commercialisation, particularly if HVDC is to be used. |  | 2022 | 2030 | L | L | L | L | LCOE reduction will be very much water depth dependent. The cost savings should be high at very deep waters (+200m) and smaller for shallow sites. | As substations are one offs (compared to WT foundations), UK could potentially develop capabilities to manufacture these. These will be large structures, that one would want to construct as close to the point of installation as possible. | This work to be led by equipment OEMs, potentially teaming up with substructure developer, due to IP considerations. Classification societies will need to be involved in this work to certify that new product meets the requirements of floating wind. | H&S could be reduced, as floating substation will never be as stable as bottom-fixed ones.
Testing methodologies for floating wind components (electrical) | Innovation Area | NO | TRL 3 | TRL 8 | Research Technical Organisations | Original Equipment Manufacturers | Enabling disruptive innovation | Background: The electrical infrastructure for floating wind components needs to resist the motions of the hull, both in terms of extreme motions and fatigue over the lifetime of the project. Additionally, floating platform substation will have to include loads resistance for low frequency, high acceleration events and larger number of fatigue cycles over its lifetime. Innovation: Electrical elements (particularly critical components of the transformer) for floating wind require further testing, development, and qualification. Industry and RTOs need to cooperate to develop suitable standards and guidelines for the testing methodologies. |  | 2022 | 2027 | M | M | H | L | Reduced OPEX. | UK-based academia and classification societies are well placed to develop methodologies and verifies these. |  | Reduced probability of component failure, resulting in reduced number of interventions by technicians.
Lead-free dynamic cables | Innovation Area | YES | TRL 3 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Commercialising>15MW turbine platforms | Background: At present offshore wind farm inter-array cables typically operate at 33kV and 66kV. At these voltage level cables do not require a lead sheath. However, cables above 66kV will require lead sheaths as a water blocking feature to prevent water ingress to the conductor. Because of this requirement, it stands as a major barrier to lead-free 132kV+ inter-array cables, with the step change to 132kV+ being highly necessary to accommodate higher turbine ratings of 20MW+ in the future. Innovation: Research is required to find suitable replacements to lead sheaths that maintain the same level of water blocking ability. JDR have received funding to develop a 132kV dynamic cable by BEIS (See AHEAD project). Efforts required here include the need to develop a 132kV dynamic cable which can be demonstrated at scale. In general a lead-free design is highly desirable for accelerating commercialisation of HV dynamic cables due to the restrictions on bend capability brought about by lead sheaths. |  | 2022 | 2027 | M | H | M | H | Larger quantities of power can be generated via higher voltage levels, resulting in lower transmission losses. | JDR set to lead the way with 132kV+ inter-array cables. High export potential for the UK. | Medium-Low. JDR received BEIS funding but this innovation is one which would gradually make way to market without additional funding.
Accelerated development of Higher-voltage Export & Array cables for Dynamic applications (AHEAD) | Ongoing R&D project | YES | TRL 1 | TRL 1 | Industry/SMEs | Owner Operators | Commercialising>15MW turbine platforms | No dynamic cable rated above 66kV has ever been deployed in an offshore wind environment. Due to increased turbine sizes, distances from shore, and water depths, in the 2020s the industry will require significantly higher voltage dynamic cables. This project aims to demonstrate the following technologies: Demonstration of innovative polymer insulation systems to be capable of operation above 66 kV and to 132 kV, potentially as a wet-design. Extension of Dynamic Array cable construction to larger and heavily Dynamic Export cables at 132 kV. Advanced dynamic cable modelling to engineer cable configurations with higher loadings or stiffer cabling. Integration of next generation optical fibre strain sensing technology into Dynamic HV Export and Array cables to improve offshore cable monitoring and maintenance. | https://www.gov.uk/government/publications/floating-offshore-wind-demonstration-programme-successful-projects/floating-offshore-wind-demonstration-programme-details-of-successful-projects | 2022 | 2027
Subsea Substation to FOW Interface assembly demonstrator | Ongoing R&D project | YES | TRL 1 | TRL 1 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | This project seeks to integrate dynamic inter-array cables manufactured using Aker Solutions’ Oscilay™ cable manufacturing technique with subsea substations capable of reducing LCOE by 20% compared to traditional topside substations. Oscilay™ cables have greater machine simplicity and require fewer splices and welds, as well as offering simpler and cheaper offshore installation. Combined with subsea substations, this has the potential to significantly increase the efficiency of energy transmission back to shore. | https://www.gov.uk/government/publications/floating-offshore-wind-demonstration-programme-successful-projects/floating-offshore-wind-demonstration-programme-details-of-successful-projects | 2022 | 2027
Offshore Substation Optimisation
Optimised Designs
Standardisation of HVAC | Innovation Area | NO | TRL 7 | TRL 9 | Industry/SMEs | Owner Operators | Commercialising>15MW turbine platforms | Background: grid integration of huge amounts of wind power is one of the main challenges ahead for the offshore wind and power network industries in the 2020s. Although some developers have already shown mover towards standardised substation designs, there are still may designs which are one of a kind. Innovation: Standardised AC Offshore Substation Designs; Lessons learned from UK and European projects and evolution from ad-hoc designs to modular repetitive solutions. |  | 2022 | 2025 | H | L | M | n/a |  |  |  | Mostly a cost concern
HVDC Convertor Platform optimisation | Innovation Area | YES | TRL 6 | TRL 8 | Industry/SMEs | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Background: grid integration of huge amounts of wind power is one of the main challenges ahead for the offshore wind and power network industries in the 2020s. Some of the economically viable areas for offshore wind development are at the limits of what is achievable with existing HVAC technology with intermediate reactive power compensation. Innovation: Designs of HVDC platforms are still not optimised leading to increased costs. Most designs include personnel to be stationed for prolonged periods of time requiring more ancillary services. It is known that this greatly increases maintenance requirements increasing costs. The size of offshore substations also limits the manufacturers and ports capable of supplying them. |  | 2022 | 2025 | H | M | M | L |  |  |  | Standardised design would result in operators being more familiar with setups and small impact on H&S
DC Arrays
MVDC Protection | Innovation Area | YES | TRL 6 | TRL 9 | Industry/SMEs | Original Equipment Manufacturers | Enabling disruptive innovation | Background: To allow the offshore interface, challenges around the offshore protection of DC networks must be addressed and demonstrated. Many different strategies are possible including DC circuit breakers, powering DC grid down etc. However, all have problems, including cost or wind farm availability. Innovation Offshore DC Array Architecture - Protection methods, breakers. Development of cost-effective protection philosophy that maximises windfarm availability and minimises cost and device size. Reduction of electrical stresses, but mechanical stresses would remain the same. Reduce number of components to reduce costs. It is a safety system, but not designed to protect human intervention |  | 2022 | 2025 | M | M | M | n/a
MVDC Interface | Innovation Area | YES | TRL 3 | TRL 5 | Academia | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Offshore substations contribute significantly to the capital cost of the offshore wind farm (15-20%). Currently most commissioning must be done offshore, leading to project delays and offer a single point of failure. Modularising and or/eliminating these offshore substructures presents an opportunity to significantly reduce costs, improve reliability and reduce commissioning time. Using MVDC, many technical issues around HVDC options have been addressed already (isolation distances etc.), therefore, for wind farms located at distances on the boundary between AC and DC transmission, this could prove to be an attractive option and available in a shorter time period than HVDC. This can be an intermediate step to HVDC Interface. Innovation: MVDC Interarray Grid (Up to equivalent of 66kV AC grid). Develop convertor, control system and switchgear within WTG or smaller set of offshore platforms to enable this new topology. |  | 2022 | 2025 | H | L | M | L |  |  | Successful intervention would increase UK benefit to High | It will slightly reduce number of equipment offshore
HVDC Interface | Innovation Area | YES | TRL 3 | TRL 5 | Academia | Original Equipment Manufacturers | Enabling disruptive innovation | Background: Offshore substations contribute significantly to the capital cost of the offshore wind farm (15-20%). Currently most commissioning must be done offshore, leading to project delays and offer a single point of failure. Modularising and or/eliminating these offshore substructures presents an opportunity to significantly reduce costs, improve reliability and reduce commissioning time. Innovation HVDC Interarray Grid (above equivalent of a 66kV AC grid). Develop convertor, control system and switchgear within WTG or smaller set of offshore platforms to enable this new topology. |  | 2022 | 2035 | H | L | M | L |  |  |  | It will slightly reduce number of equipment offshore
Alternatives to substation
Subsea power substation | Innovation Area | YES | TRL 2 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Commercialising>15MW turbine platforms | Power substations are currently based above the sea level and require heavy and long foundations. Innovation: Some industry players have an AC substation platform under development which is adapting oil and gas technology for offshore wind purposes. They are also working on developing a HVDC substation platform, but it is not as well advanced. Challenges that are around subsea substations include the ability/challenges of maintaining/replacing components within the converter. |  | 2022 | 2040 | M | L | M | H
Energy Islands | Innovation Area | YES | TRL 5 | TRL 9 | Industry/SMEs | Owner Operators | Enabling disruptive innovation | Energy islands serve as an offshore power hub collecting, storing, converting and distributing green electricity from hundreds of offshore wind turbines directly to consumers and countries bordering the island. Danish government plans to establish two large-scale offshore wind farm projects or "energy islands“ by the year 2030. These are set to be developed by TenneT, Energinet and Gasunie in the Baltic and North Sea. Energy islands offer an alternative to offshore substations allowing multiple wind farms or indeed other energy sources to be interfaced and sent to shore via power cables or Hydrogen. |  | 2022 | 2030 | M | M | H | H | By providing a central location for multiple wind projects to interface it is hoped that offshore infrastructure costs can be reduced and interconnectivity increased | Energy islands in the North Sea will likely be connected to the UK allowing more wind connected energy at a cheaper cost. There is also the opportunity for UK firms to be involved in the manufacture and operation of the islands. | The energy islands are already being taken forward by industry | The islands will have proper harbours and personnel will be based on "dry land" reducing risks.
Turbine Platforms | Innovation Area | YES | TRL 3 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Commercialising>15MW turbine platforms | Cost reductions of electrical infrastructure can be achieved by increasing the collection grid voltage from 33-36 kV AC to 66-72 kV AC for large offshore wind farms. These include reduction of capital costs for both radial and inter-array cables, implementation of ring array systems and reduction of the number of offshore substations. For small and medium, close-to-shore wind power plants, it might be cost effective to connect wind turbines to onshore substations directly by 66-72 kV AC cables. Concepts of platformless DC connections of offshore wind turbines would offer more cost-effective solutions in many cases when compared to the AC collection and transmission solutions. The key technology of such direct DC connection solutions is to use a wind turbine drivetrain that would produce high enough DC voltage output and transmit the power directly onshore with DC cables. AC turbine platforms are already in use by some industry players, but DC versions of this are still some way off. |  | 2022 | 2040 | H | M | H | L | Offshore platforms are a major cost and provide a single source of failure. Turbine mounted platforms eliminate many of the associated costs with only marginal increasing in turbine structural requirements | UK can benefit from the technology. UK also has existing industry in the HVDC space (GE Grid) | This is a significant change from the current setup and intervention will be required to bring it to the industry | Personnel still required to go offshore to fix issues
Enabling Research
Digitalisation and Information Systems
Machine learning | Innovation Area | NO | TRL 3 | TRL 6 | Academia | Owner Operators | Enabling disruptive innovation | Make use of machine learning applications and draw benefit from disparate data sources to optimise OWF operation strategies. Challenges to be addressed when making use of machine learning applications include the integration and validation of numerical models with sensor data to come up with accurate interpretation or diagnostics of phenomena or activities of interest. |  | 2022 | 2025 | M | H | H | M |  | Potentially an area where the UK can be a real leader |  | Optimised O&M operations
Internet of things | Innovation Area | NO | TRL 3 | TRL 9 | SME | Owner Operators | Enabling disruptive innovation | Internet of Things involves an increased level of interaction and communication between measurement systems and components being monitored. it is seen as an evolution to current capabilities of condition and health monitoring technologies. Major challenges include reliability and calibration of sensor systems as well as security and access to information. There is requirement of coordination of work between RTOs, Academia and Industry/SMEs. |  | 2022 | 2030 | M | M | H | L | This will involve system integration of SCADA and SHM systems | Unlikely to involve protected IP, more likely to result in communications protocols and standards/best practice.
Artificial Intelligence | Innovation Area | NO | TRL 1 | TRL 6 | Academia | Owner Operators | Enabling disruptive innovation | Artificial Intelligence can have multiple applications in all stages of windfarm lifecycle. Taking O&M as an example – AI application involves a supervisory system that utilises conventional design and operation rules combined with Machine Learning/Deep learning from big data from the internet of things. AI could be a decision support system or a complete framework for collecting information and acting upon this without human intervention. Challenges are verification/validation of AI systems and quantitative assessment of confidence in AI performance. Other examples could include design optimisation, turbine control, Turbine Yaw Error and Control, Grid Balancing or Transmission Fault Diagnostics and Prognostics. |  | 2022 | 2035 | H | M | M | H
Data utilisation | Innovation Area | NO | TRL 3 | TRL 6 | Research Technical Organisations | Original Equipment Manufacturers | Maximising operational performance of existing wind farms | Data utilisation is an overarching term used to describe a wide range of concepts and techniques aimed at exploiting available information. In this context data utilisation is performed with the aim of data-driven decision making. In the offshore renewables Industry/SMEs, data utilisation techniques can include: post-event analysis, use of current operational data and forecasting of future trends. The level of data utilisation is varied across Industry/SMEs, providing the opportunity for innovation and collaboration between offshore wind stakeholders. |  | 2022 | 2030 | M | M | M | L | This depends on the engagement by OOs and the impact their use of data has. | UK has high expertise in this field and can actively engage in data and digital activities. | Although some OOs do actively engage in data utilisation activities, some will need external bodies to help kickstart a culture change within their organisation. | Optimised O&M operations
Design and materials
Innovation in design concepts | Innovation Area | YES | TRL 1 | TRL 4 | Academia | Owner Operators | Enabling disruptive innovation | Exploring how potential large arrays located far from shore farms (wind, tidal and wave) might lead to different optimal design concepts than those already adopted. |  | 2022 | 2036 | M | H | H | M |  | Totally new design concept could be developed and UK could export knowhow, R&D and potentially manufacture of new-concept turbines. | Due to the low TRL, this must be driven by academia, but the participation of Industry/SMEs is critical to assure significance and relevance of the proposed concepts. | Results are unknown yet as it will depend on a design
Design for marine life and aquaculture | Innovation Area | YES | TRL 2 | TRL 5 | Academia | Owner Operators | Enabling disruptive innovation | Currently, the design process of a turbine, an array and associated infrastructure does not take into account the potential to enhance marine life (biodiversity), contribute to fisheries sustainability or aquaculture production. This process may have conservation value and may provide nursery areas for commercially relevant fish and shellfish, but there is a need to undertake research to assess the potential value of this process. In the longer term, this could contribute to the sustainability of local fishing opportunities. The use of offshore renewable sites for aquaculture has been explored in principle and through some limited trials, but there are likely to be significant logistical, biological and economic challenges to successful, commercial deployment. There is opposition to renewables developments that are perceived or in reality compromise fishing activity. Developing clear and demonstrable pathways to achieving these objectives could potentially help to streamline consenting and licencing processes and perhaps more importantly secure social license. There are potentially significant cost savings in this process. |  | 2022 | 2033 | L | M | M | H |  | This element wouldn’t drive LCOE down but could enable additional revenue generation. Successful design could boost fishing Industry/SMEs confidence to go back to fishing grounds. | Links to sustaining a strong commercial fishing Industry/SMEs
Self-healing materials | Innovation Area | YES | TRL 3 | TRL 5 | Academia | Original Equipment Manufacturers | Enabling disruptive innovation | Development of materials that can maintain their integrity and self-heal when deficiencies occur due to material degradation. Materials could be applicable to any asset that's exposed to environmental conditions: blades, tower, substructures, cables. In electrical infrastructure power cable failure in wet environments arises most frequently from damage to the protective sheath or jacket layers allowing rapid water ingress. |  | 2022 | 2038 | H | H | M | L |  |  |  | May reduce number of minor repairs